## Fire Alarm
FIRE ALARM | [6 empty] | STATUS
| Confidence Test |  | Deficiency Repair Test |  |  |  |  | Red | Yellow |  | White
Occupancy Information
Premises Name: | [6 empty] | Premises Address:
Contact Name: | [6 empty] | Contact Phone:
Contact Address: | [6 empty] | Contact Email:
Central Station Monitoring: |  |  |  | Yes |  | No | Monitoring Required: |  |  | Yes |  | No
Monitoring Company Name: | [6 empty] | Internal Dialer? |  |  | Yes |  | No
Monitoring Company Phone: | [6 empty] | AES/Radio? |  |  | Yes |  | No
Fire Alarm Inventory (M-mandatory)
Fire Alarm Panel Unit ID (TCE will assign one per system) (M):
Smoke Detector Sensitivity (required every 5 yrs, after passing 1st annual calibration test) – Last Test Date (month/year):
Smoke Detector Sensitivity – Test Due Date (month/year):
FACP & Annunciators
Fire Alarm Control Panel/Unit Location (M):
| Fire Alarm Panel Brand: | [5 empty] | Fire Alarm Panel Model:
| FACP – location of key (M): | [5 empty] | Annunciator location (M): |  |  |  |  | N/A
| Notification Power Expander(s) Installed? |  |  | Yes |  | No | Notification Power Expander(s) Location:
Note: This section is optional except at time of new system acceptance. Please enter number of devices or items in the system. Should match U.L. label.
Initiating Devices |  |  |  | # of devices/items | [5 empty] | # of devices/items
| Beam detectors | [5 empty] | Smoke detectors - Regular
| Duct detectors | [5 empty] | Smokes – above ceiling
| Heat tape supervisory signals | [5 empty] | Smokes – under floor
| Heats – above ceiling | [5 empty] | Sprinkler flow switches
| Heats – regular | [5 empty] | Sprinkler valve tamper switches
| Heats – under floor | [5 empty] | High/low air switches
| Pull stations (manual stations) | [5 empty] | Other supervisory switches
Notification Devices
| Bells, chimes | [5 empty] | Horn/strobe combo
| Exterior sprinkler alarm bell | [5 empty] | Horns only
Auxiliary Equipment | [6 empty] | Strobes only
| Auto door release | [5 empty] | Fire/smoke dampers
| Auto door unlock | [5 empty] | Generators
| Elevator recall | [5 empty] | Ventilation controls
| Fire doors | [5 empty] | Other (DAS/Vesda…)
| Fire fighter phone jacks | [5 empty] | Other (DAS/Vesda…)
| Fire fighter phone sets | [5 empty] | Other (DAS/Vesda…)
Stairway Door Locks
| Electric bolt | [5 empty] | Other locking devices
| Electric strike | [5 empty] | Stairwell egress devices
Battery Info
| Date Installed (month/year): | [5 empty] | Date due for next testing (month/year):
| Number of batteries: | [5 empty] | Battery Size (AH):
Inspection & Testing Agency Information
Company Name: | [6 empty] | Phone:
Address: | [6 empty] | Emergency Phone:
Email:
Inspector/Tester Information
Inspector Name:
Certification No.:
Test Information
Date of Test:
Test Type: |  | Annual |  |  | Quarterly |  |  | Semi-annual | Monthly
Area of building tested and general description of testing performed on this report (text field)
This is the final report for the testing year, indicating completion of 100% of the mandatory tests. (Reports confirming tests of 100% of devices must be submitted annually.) | [9 empty] | Yes |  | No
The items on the checklists below shall be inspected and tested. This list does not constitute all of the required inspecting and testing of the fire and life safety system. Refer to the CURRENT FIRE CODE AND REFERENCED NFPA 72 STANDARD and the MANUFACTURER'S INSTRUCTIONS for weekly, monthly, and quarterly inspecting and testing requirements. ONLY SELECT N/A FOR ITEMS THAT DO NOT EXIST AT THE BUILDING, DO NOT USE N/A TO INDICATE THAT A TEST OR RESULT IS NOT AVAILABLE.
PRE-TEST CHECKS
AVOID UNNECESSARY ALARMS BY PUTTING THE FIRE ALARM SYSTEM IN TEST MODE. Failure to place the Fire Alarm System (FAS) into test mode and/or taking other precautions to may cause preventable alarms.
1 | The building occupants were notified. | [7 empty] | Yes | No |  | N/A
2 | The onsite supervisory station was notified. | [7 empty] | Yes | No |  | N/A
3 | The Central Station Monitoring Service was notified to place FAS in test mode. | [7 empty] | Yes | No |  | N/A
GENERAL
4 | The key to the panel is available at the FACP. | [7 empty] | Yes | No |  | N/A
5 | The operating instructions are available at the FACP. | [7 empty] | Yes | No
6 | Materials and equipment needed to restore pull stations are available at the main panel, e.g. glass rods, and plates; keys and allen wrenches, etc. | [7 empty] | Yes | No |  | N/A
ALARM PANEL
7 | The FACP operates on AC power. | [7 empty] | Yes | No
8 | If the system has batteries, the FACP operates on Battery power. | [7 empty] | Yes | No |  | N/A
9 | If the system has emergency generator/standby power, the FACP operates on emergency generator/standby power. | [7 empty] | Yes | No |  | N/A
10 | If the system has battery or standby power, the trouble indicators function properly and a trouble signal comes on with AC power off. | [7 empty] | Yes | No |  | N/A
INITIATING DEVICES AND NOTIFICATION APPLIANCES
11 | Initiating & notification appliances tested operate properly on AC power. | [7 empty] | Yes | No
12 | If system has generator/standby power, initiating and notification appliances tested operate properly on generator/standby power. | [7 empty] | Yes | No |  | N/A
13 | If system has batteries, initiating and notification appliances tested operate properly on battery power. | [7 empty] | Yes | No |  | N/A
14 | 100% of the INITIATING DEVICES per circuit that were tested and included as part of this report were in accordance with the NFPA 72 Chapter 14 standards referenced by the current fire code. | [7 empty] | Yes | No
Note: 2 or 20%, whichever is greater, of restorable fixed-temperature, spot-type heat detectors need to be tested annually. Records shall be kept to ensure that every detector is tested every five years.
15 | The sensitivity test for smoke detectors is up-to-date in accordance with NFPA 72. (After passing the 2nd required calibration test, sensitivity may be calibrated once every 5 years [2016 NFPA 72 Sec 14.4.4.3]). | [7 empty] | Yes | No |  | N/A (w/ req'd comment)
Date most recent smoke detector sensitivity test was passed:
16 | 100% of the AUDIBLE NOTIFICATION APPLIANCES per circuit that were tested and included as part of this report were in accordance with 2016 NFPA 72 Chapter 14. | [7 empty] | Yes | No
17 | The audible notification appliances tested operate at the levels required by NFPA 72. | [7 empty] | Yes | No
18 | The audible notification appliances tested in residential units generate a minimum of 60DBA at the pillow in the sleeping areas. | [7 empty] | Yes | No |  | N/A
19 | 100% of the VISUAL NOTIFICATION APPLIANCES per circuit that were tested and included as part of this report were in accordance with 2016 NFPA 72 Chapter 14. Only select N/A if no such devices in building. | [7 empty] | Yes | No |  | N/A
BATTERIES
20 | Battery voltage (no load):
21 | Battery voltage (full load):
22 | New batteries installed? |  |  |  | Battery installation date: [current month/year]:
23 | Charge circuit voltage:
INTERFACE DEVICES
The FACP received signals from the following Interface devices: Tested by: | [8 empty] | Simulation |  | Operation
24 | Emergency Generator(s) | [7 empty] | Yes | No |  | N/A
25 | Flow Switch(es) | [7 empty] | Yes | No |  | N/A
26 | Supervisory Switch(es) | [7 empty] | Yes | No |  | N/A
27 | Range Hood Suppression System(s) | [7 empty] | Yes | No |  | N/A
28 | Dry Chemical System(s) | [7 empty] | Yes | No |  | N/A
29 | Clean Agent System(s) | [7 empty] | Yes | No |  | N/A
30 | Pre-action Systems(s) | [7 empty] | Yes | No |  | N/A
31 | Pull Stations | [7 empty] | Yes | No |  | N/A
OTHER EQUIPMENT CONTROLLED BY FACP
The following Fire Safety Functions responded to signals from the FACP: Tested by: | [8 empty] | Simulation |  | Operation
Note: This section replaces the Sequence Test Form. The checks in this section are only required during one of the quarterly tests. The functions in this section require testing during the annual confidence test for all other buildings.
32 | Fan controls | [7 empty] | Yes | No |  | N/A
33 | Smoke Dampers | [7 empty] | Yes | No |  | N/A
34 | Elevator Recall system | [7 empty] | Yes | No |  | N/A
35 | Elevator Shunt Switch(es) | [7 empty] | Yes | No |  | N/A
36 | Magnetic Door Holders | [7 empty] | Yes | No |  | N/A
37 | Door Lock devices | [7 empty] | Yes | No |  | N/A
38 | Fire Pump(s) | [7 empty] | Yes | No |  | N/A
39 | General alarm automatic time delay |  |  |  |  | (minutes) |  |  | Yes | No |  | N/A
40 | Remote Annunciator Panels | [7 empty] | Yes | No |  | N/A
COMMUNICATION EQUIPMENT
41 | All phone sets function properly. | [7 empty] | Yes | No |  | N/A
42 | All phone jacks function properly. | [7 empty] | Yes | No |  | N/A
43 | All phone indicating signals at the FACP work properly. | [7 empty] | Yes | No |  | N/A
44 | The public address equipment at the FACP works properly. | [7 empty] | Yes | No |  | N/A
ALARM PANEL MONITORING
45 | A signal was received at the Central Station monitoring company. | [7 empty] | Yes | No |  | N/A
STAIRWAY DOOR LOCKS [if no stairways in building, skip this section and proceed to final checks]
This building has stairways: | [8 empty] | Yes |  |  | N/A
46 | All stairway door locking devices release simultaneously, without unlatching, upon activation of the fire alarm system from anywhere in the building. | [7 empty] | Yes | No |  | N/A
47 | All stairway door locking devices release simultaneously, without unlatching, upon activation from the fire command center. | [7 empty] | Yes | No |  | N/A
48 | The door(s) to the roof unlocks upon activation of the fire alarm system. | [7 empty] | Yes | No |  | N/A
49 | There is an access key at the control panel for doors that fail to unlock. | [7 empty] | Yes | No |  | N/A
50 | All of the doors open, close, and latch properly. | [7 empty] | Yes | No |  | N/A
FINAL CHECKS, MANDATORY TAGGING, AND REPORTS
Put the Fire Alarm back into service and/or other precautionary measures that were made to restore fire alarm system to normal operation (includes removal of protective coverings.)
51 | A current red, yellow or white tag was placed at the fire alarm control panel indicating the system’s status consistent with my inspection today and SFD Administrative Rule 9.02. | [7 empty] | Yes | No
| The color of the tag is: | [7 empty] | Red | Yellow |  | White
52 | I will provide a copy of the confidence test report to the owner. | [7 empty] | Yes | No
53 | I will submit this test report to the fire department through TCE. | [7 empty] | Yes | No
By accepting this statement I, the certified technician shown on this form, certify that this fire protection system(s) has been properly inspected for functional operation in accordance with the current Fire Code (FC) used by the department that has jurisdiction and NFPA Standards adopted by the FC for this system. Any deficiencies found are noted in the report and have been reported to the building Owner/Manager for corrective action.
| I accept. | I am authorized to submit this report for the certified technician who has accepted this statement. | [6 empty] | (Initials of Employee)
SIGNATURE (OPTIONAL)
Signature of Technician
Signature of Building Representative
System Testing Reports Must Be Submitted Online
Submit reports to http://www.thecomplianceengine.com/
FIRE ALARM SYSTEM TEST REPORT
(05/2020)